## Guideline Calculator
Safety Guideline for Indoor Airborne Transmission of COVID-19
Martin Z. Bazant
Contact: | bazant@mit.edu |  | http://www.mit.edu/~bazant
History: 6-4-2020 (v1), 7-1-2020 (v2), | 8-16-2020 (v3), medRxiv 9-1-20 (v4), 10-20-2020 (v5)
This version: 1-11-2021 (v6)
For an online app, edX course other resources, please visit: |  |  | http://www.mit.edu/~bazant/COVID-19
Reference: Martin Z. Bazant and John W. M. Bush, medRxiv preprint (2020)
"Beyond Six Feet: A Guideline to Limit Indoor Airborne Transmission of COVID-19"
https://doi.org/10.1101/2020.08.26.20182824 |  | (Instructions in the Supporting Information, Sec. 6.)
Input values in the pink cells.
Physical Parameters
Floor area, A | 900 | ft2 | 83.6127 | m2
Mean ceiling height, H | 12 | ft | 3.6576 | m
Room volume, V | 10800 | ft3 | 305.8219 | m3
Outdoor air exchange rate, la | 3 | /hr (ACH)
Ventilation (outdoor air) flow rate, Q | 540 | ft3/min | 917.4658 | m3/hr
Recirculation air exchange rate, lr | 3 | /hr (ACH) | (includes HVAC & air filtration units)
Recirculation (return) flow rate, Qr | 540 | ft3/min | 917.4658 | m3/hr
Primary (total) air flow rate, Q+Qr | 1080 | ft3/min | 1834.9317 | m3/hr
Primary outdoor air fraction, Zp | 0.5 | (=1.0 natural ventilation, or no recirculation)
Aerosol filtration efficiency, pf | 0.8 | (>0.9997 HEPA, =0.2-0.9 MERVs, =0 no filter)
Air filtration rate, lf | 2.4 | /hr
Relative humidity, RH | 50 | %
Physiological Parameters
Mean breathing flow rate, Qb | 0.29429 | ft3/min | 0.5 | m3/hr (=0.5 rest, =1-3 active)
Respiratory aerosol radius, r | 2 | mm | (depends weakly on activity, disease)
Humidity-adjusted radius | 1.8566 | mm
Disease Parameters
Infectiousness of exhaled air, Cq | 30 | infection quanta/m3 |  | (depends on activity, Fig. 2)
Viral deactivation rate, lv @ 50% RH | 0.3 | /hr | 3.3333 | hour deactivation time
Humidity-adjusted deactivation rate | 0.3 | /hr | (assume linear in RH)
Relative transmissibility, sr | 0.68 | (=0.23 for children, 0.68 for adults, 1.0 for elderly,
multiply by 1.58 for B.1.1.7 UK variant of concern)
Infectious Aerosol Properties
Effective settling speed, vs(r) | 0.41365 | mm/sec | 1.4891 | m/hr.
Concentration relaxation rate, lc | 6.1071 | /hr | 0.16374 | hour relaxation time
Dilution factor, fd | 0.00026771 | infectiousness of ambient air / exhaled breath
Infectiousness of room air, fd Cq | 0.0080313 | infection quanta/m3 in steady state
Precautionary Parameters
Mask aerosol passage probability, pm | 0.2 | (=1 no masks, 0.1 standard, 0.3 poor compliance)
Airborne transmission rate, ba | 7.4273e-05 | /hr | (per pair of persons in steady state)
Risk tolerance, e | 0.1 | (bound on Rin, expected transmissions per infector)
Safe Room Occupancy
Exposure time, t | 40 | hours | (net before testing/removal/recovery)
Maximum safe occupancy, Nmax | 34 | persons | (with transient aerosol buildup)
| 34 | persons | (steady state aerosol concentration)
6 FOOT RULE (CDC) | 25 | persons
1 METER RULE (WHO) | 83 | persons
Maximum occupancy for outdoor air | 45 | persons
Minimum outdoor airflow / person | 12 | ft3/min | 5.6634 | L/s
Safe Exposure Time
Room occupancy, N | 25 | persons
Maximum exposure time, tmax | 56.2624 | hours | 3375.7429 | minutes (transient)
| 56.0991 | hours | 3365.9468 | minutes (steady state)

## Plot Data
t (hours) | N | Transient cumulative exposure time bound
0 | 10000 | epsilon | beta_a | lambda_c | N (6 ft rule) | 1.8754 | dtau
1.8754 | 781.5916 | 0.1 | 7.4273e-05 | 6.1071 | 25
3.7508 | 375.6256 | 0.1 | 7.4273e-05 | 6.1071 | 25
5.6262 | 247.2681 | 0.1 | 7.4273e-05 | 6.1071 | 25
7.5017 | 184.3952 | 0.1 | 7.4273e-05 | 6.1071 | 25
9.3771 | 147.0894 | 0.1 | 7.4273e-05 | 6.1071 | 25
11.2525 | 122.3929 | 0.1 | 7.4273e-05 | 6.1071 | 25
13.1279 | 104.8379 | 0.1 | 7.4273e-05 | 6.1071 | 25
15.0033 | 91.7182 | 0.1 | 7.4273e-05 | 6.1071 | 25
16.8787 | 81.5417 | 0.1 | 7.4273e-05 | 6.1071 | 25
18.7541 | 73.4179 | 0.1 | 7.4273e-05 | 6.1071 | 25
20.6295 | 66.7826 | 0.1 | 7.4273e-05 | 6.1071 | 25
22.505 | 61.2612 | 0.1 | 7.4273e-05 | 6.1071 | 25
24.3804 | 56.5948 | 0.1 | 7.4273e-05 | 6.1071 | 25
26.2558 | 52.5991 | 0.1 | 7.4273e-05 | 6.1071 | 25
28.1312 | 49.1393 | 0.1 | 7.4273e-05 | 6.1071 | 25
30.0066 | 46.1143 | 0.1 | 7.4273e-05 | 6.1071 | 25
31.882 | 43.4469 | 0.1 | 7.4273e-05 | 6.1071 | 25
33.7574 | 41.0774 | 0.1 | 7.4273e-05 | 6.1071 | 25
35.6328 | 38.9584 | 0.1 | 7.4273e-05 | 6.1071 | 25
37.5083 | 37.0522 | 0.1 | 7.4273e-05 | 6.1071 | 25
39.3837 | 35.3284 | 0.1 | 7.4273e-05 | 6.1071 | 25
41.2591 | 33.7618 | 0.1 | 7.4273e-05 | 6.1071 | 25
43.1345 | 32.332 | 0.1 | 7.4273e-05 | 6.1071 | 25
45.0099 | 31.0218 | 0.1 | 7.4273e-05 | 6.1071 | 25
46.8853 | 29.8167 | 0.1 | 7.4273e-05 | 6.1071 | 25
48.7607 | 28.7047 | 0.1 | 7.4273e-05 | 6.1071 | 25
50.6361 | 27.6753 | 0.1 | 7.4273e-05 | 6.1071 | 25
52.5116 | 26.7196 | 0.1 | 7.4273e-05 | 6.1071 | 25
54.387 | 25.8301 | 0.1 | 7.4273e-05 | 6.1071 | 25
56.2624 | 25 | 0.1 | 7.4273e-05 | 6.1071 | 25
58.1378 | 24.2236 | 0.1 | 7.4273e-05 | 6.1071 | 25
60.0132 | 23.4959 | 0.1 | 7.4273e-05 | 6.1071 | 25
61.8886 | 22.8124 | 0.1 | 7.4273e-05 | 6.1071 | 25
63.764 | 22.1692 | 0.1 | 7.4273e-05 | 6.1071 | 25
65.6394 | 21.5629 | 0.1 | 7.4273e-05 | 6.1071 | 25
67.5149 | 20.9903 | 0.1 | 7.4273e-05 | 6.1071 | 25
69.3903 | 20.4488 | 0.1 | 7.4273e-05 | 6.1071 | 25
71.2657 | 19.9358 | 0.1 | 7.4273e-05 | 6.1071 | 25
73.1411 | 19.4492 | 0.1 | 7.4273e-05 | 6.1071 | 25
75.0165 | 18.9869 | 0.1 | 7.4273e-05 | 6.1071 | 25
76.8919 | 18.5473 | 0.1 | 7.4273e-05 | 6.1071 | 25
78.7673 | 18.1286 | 0.1 | 7.4273e-05 | 6.1071 | 25
80.6427 | 17.7295 | 0.1 | 7.4273e-05 | 6.1071 | 25
82.5182 | 17.3485 | 0.1 | 7.4273e-05 | 6.1071 | 25
84.3936 | 16.9845 | 0.1 | 7.4273e-05 | 6.1071 | 25
86.269 | 16.6364 | 0.1 | 7.4273e-05 | 6.1071 | 25
88.1444 | 16.3031 | 0.1 | 7.4273e-05 | 6.1071 | 25
90.0198 | 15.9837 | 0.1 | 7.4273e-05 | 6.1071 | 25
91.8952 | 15.6773 | 0.1 | 7.4273e-05 | 6.1071 | 25
93.7706 | 15.3833 | 0.1 | 7.4273e-05 | 6.1071 | 25
95.646 | 15.1008 | 0.1 | 7.4273e-05 | 6.1071 | 25
97.5215 | 14.8292 | 0.1 | 7.4273e-05 | 6.1071 | 25
99.3969 | 14.5678 | 0.1 | 7.4273e-05 | 6.1071 | 25
101.2723 | 14.3161 | 0.1 | 7.4273e-05 | 6.1071 | 25
103.1477 | 14.0736 | 0.1 | 7.4273e-05 | 6.1071 | 25
105.0231 | 13.8398 | 0.1 | 7.4273e-05 | 6.1071 | 25
106.8985 | 13.6142 | 0.1 | 7.4273e-05 | 6.1071 | 25
108.7739 | 13.3964 | 0.1 | 7.4273e-05 | 6.1071 | 25
110.6494 | 13.186 | 0.1 | 7.4273e-05 | 6.1071 | 25
112.5248 | 12.9826 | 0.1 | 7.4273e-05 | 6.1071 | 25
114.4002 | 12.7859 | 0.1 | 7.4273e-05 | 6.1071 | 25
116.2756 | 12.5955 | 0.1 | 7.4273e-05 | 6.1071 | 25
118.151 | 12.4112 | 0.1 | 7.4273e-05 | 6.1071 | 25
120.0264 | 12.2327 | 0.1 | 7.4273e-05 | 6.1071 | 25
121.9018 | 12.0596 | 0.1 | 7.4273e-05 | 6.1071 | 25
123.7772 | 11.8918 | 0.1 | 7.4273e-05 | 6.1071 | 25
125.6527 | 11.729 | 0.1 | 7.4273e-05 | 6.1071 | 25
127.5281 | 11.5711 | 0.1 | 7.4273e-05 | 6.1071 | 25
129.4035 | 11.4177 | 0.1 | 7.4273e-05 | 6.1071 | 25
131.2789 | 11.2687 | 0.1 | 7.4273e-05 | 6.1071 | 25
133.1543 | 11.1239 | 0.1 | 7.4273e-05 | 6.1071 | 25
135.0297 | 10.9831 | 0.1 | 7.4273e-05 | 6.1071 | 25
136.9051 | 10.8462 | 0.1 | 7.4273e-05 | 6.1071 | 25
138.7805 | 10.7129 | 0.1 | 7.4273e-05 | 6.1071 | 25
140.656 | 10.5833 | 0.1 | 7.4273e-05 | 6.1071 | 25
142.5314 | 10.457 | 0.1 | 7.4273e-05 | 6.1071 | 25
144.4068 | 10.3341 | 0.1 | 7.4273e-05 | 6.1071 | 25
146.2822 | 10.2143 | 0.1 | 7.4273e-05 | 6.1071 | 25
148.1576 | 10.0975 | 0.1 | 7.4273e-05 | 6.1071 | 25
150.033 | 9.9837 | 0.1 | 7.4273e-05 | 6.1071 | 25
151.9084 | 9.8726 | 0.1 | 7.4273e-05 | 6.1071 | 25
153.7838 | 9.7643 | 0.1 | 7.4273e-05 | 6.1071 | 25
155.6593 | 9.6586 | 0.1 | 7.4273e-05 | 6.1071 | 25
157.5347 | 9.5554 | 0.1 | 7.4273e-05 | 6.1071 | 25
159.4101 | 9.4547 | 0.1 | 7.4273e-05 | 6.1071 | 25
161.2855 | 9.3563 | 0.1 | 7.4273e-05 | 6.1071 | 25
163.1609 | 9.2601 | 0.1 | 7.4273e-05 | 6.1071 | 25
165.0363 | 9.1662 | 0.1 | 7.4273e-05 | 6.1071 | 25
166.9117 | 9.0743 | 0.1 | 7.4273e-05 | 6.1071 | 25
168.7871 | 8.9845 | 0.1 | 7.4273e-05 | 6.1071 | 25
170.6626 | 8.8967 | 0.1 | 7.4273e-05 | 6.1071 | 25
172.538 | 8.8108 | 0.1 | 7.4273e-05 | 6.1071 | 25
174.4134 | 8.7267 | 0.1 | 7.4273e-05 | 6.1071 | 25
176.2888 | 8.6444 | 0.1 | 7.4273e-05 | 6.1071 | 25
178.1642 | 8.5639 | 0.1 | 7.4273e-05 | 6.1071 | 25
180.0396 | 8.485 | 0.1 | 7.4273e-05 | 6.1071 | 25
181.915 | 8.4078 | 0.1 | 7.4273e-05 | 6.1071 | 25
183.7904 | 8.3321 | 0.1 | 7.4273e-05 | 6.1071 | 25
185.6659 | 8.258 | 0.1 | 7.4273e-05 | 6.1071 | 25
187.5413 | 8.1854 | 0.1 | 7.4273e-05 | 6.1071 | 25
189.4167 | 8.1142 | 0.1 | 7.4273e-05 | 6.1071 | 25
191.2921 | 8.0444 | 0.1 | 7.4273e-05 | 6.1071 | 25
193.1675 | 7.9759 | 0.1 | 7.4273e-05 | 6.1071 | 25
195.0429 | 7.9088 | 0.1 | 7.4273e-05 | 6.1071 | 25
196.9183 | 7.8429 | 0.1 | 7.4273e-05 | 6.1071 | 25
198.7937 | 7.7783 | 0.1 | 7.4273e-05 | 6.1071 | 25
200.6692 | 7.7149 | 0.1 | 7.4273e-05 | 6.1071 | 25
202.5446 | 7.6527 | 0.1 | 7.4273e-05 | 6.1071 | 25
204.42 | 7.5916 | 0.1 | 7.4273e-05 | 6.1071 | 25
206.2954 | 7.5316 | 0.1 | 7.4273e-05 | 6.1071 | 25
208.1708 | 7.4728 | 0.1 | 7.4273e-05 | 6.1071 | 25